## BOQ
Trade | BOQ | Category | Task Number | Description | Total Price (USD) | Total Price (EUR) | Total Price (EGP)
[5 empty] | 13147361 | 1435207 | 670173518
Main BOQ | Main BOQ
GIS - 220KV - (Annex I) | GIS - 220KV - (Annex I) |  | 1 | Lump sum price for design, fabrication, factory testing, training and site delivery of 220 kV GIS switchgear
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.Main | 220 kV GIS switchgear
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.1 | Three phase 220 kV SF6 insulated double sectionalized bus bars and connectors with all accessories. | 166300
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.2 | Local control panels associated with the 220 kV GIS switchyard bays as specified. | 103274
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.3 | Three single phase GIS high speed earthing switch for Bus Bar 63 kA short circuit. | 45218
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.4 | Three single phase GIS inductive voltage transformer complete with its disconnector and earthing switch as specified for busbars. | 90436
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.5 | Three single phase GIS longitudinal bus bar disconnector with rated current 3150 A for the sectionalizer. | 158262
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.6 | Three single phase GIS circuit breaker for bus coupler 3150 A. | 91449
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.7 | Three single phase GIS busbar disconnectors for bus coupler 3150 A. | 67827
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.8 | Three single phase GIS maintenance earth switch for bus coupler. | 45218
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.9 | Single phase current transformers for coupler bay with two protection cores. | 67827
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.01 | Single phase current transformer for coupler bay with one protection core and one measuring core. | 67827
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.11 | Three single phase GIS longitudinal bus bar disconnector with rated current 3150 A complete with earth switch for future extension. | 88175
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.12 | Three single phase GIS circuit breakers 2500 A for OHTL feeders. | 367466
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.13 | Three single phase GIS busbar disconnectors 2500 A for OHTL feeders. | 274925
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.14 | Three single phase GIS line disconnectors 2500 A for OHTL feeders. | 137462
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.15 | Three single phase GIS maintenance earthing switch for OHTL feeders. | 144697
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.16 | Three single phase GIS high speed earthing switch for OHTL feeders. | 36174
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.17 | 220 kV single phase SF6Air bushings for OHTL feeders. | 90436
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.18 | Three single phase 220 kV SF6 insulated GIB up to the SF6Air bushing for OHTL feeders. | 27131
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.19 | Three single phase GIS circuit breakers 2500 A for cable feeders. | 177688
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.02 | Three single phase GIS busbar disconnectors 2500 A for cable feeders. | 137303
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.21 | Three single phase GIS line disconnectors 2500 A for cable feeders. | 68731
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.22 | Three single phase GIS maintenance earthing switch for cable feeders. | 72131
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.23 | Three single phase GIS high speed earthing switch for cable feeders. | 18087
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.24 | Three single phase GIS inductive voltage transformer complete with disconnector and earthing switch for cable feeders. | 45218
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.25 | Three single phase 220 kV SF6 insulated GIB up to the SF6 cable end box for cable feeders. | 27131
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.26 | Singlephase GIS surge arresters 198 kV, 20 kA, 10 kJkV with disconnector switch. | 48000
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.27 | Singlephase GIS Cable End Box for cable sealing end SF6XLPE ≥2500 A. | 180000
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.28 | Single phase current transformer for OHTL and Cable feeders. | 406962
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.29 | Three single phase GIS circuit breakers 1600 A for transformer feeder. | 177688
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.03 | Three single phase GIS Bus Bar disconnector 1600 A for transformer feeder. | 137463
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.31 | Three single phase GIS maintenance earthing switch for transformer feeder. | 72349
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.32 | Single phase current transformer for transformer feeder bays. | 135654
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.33 | 220 kV single phase SF6Air bushings for transformer feeders. | 45218
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.34 | Three phase SF6 insulated GIB up to the SF6Air bushing for transformer feeder. | 27131
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.35 | 220 kV insulating gas handling monitoring systems as specified. | 18783
ELECTRICAL WORKS | Main BOQ | GIS - 220KV | 1.36 | Sensors of SF6 partial discharge measurements as specified. | 17217
175 MVA Transformer - (Annex II) | 175 MVA Transformer - (Annex II) |  | 2 | Lump sum price of two 2 three phase 2206611 kV Power Transformers each of 175 MVA
ELECTRICAL WORKS | Main BOQ | 175 MVA Transformer | 2.Main | 175 MVA Power Transformers
ELECTRICAL WORKS | Main BOQ | 175 MVA Transformer | 2.1 | Threephase oilimmersed outdoor power transformers 175 MVA, 2206611 kV complete with accessories. | 4188748
ELECTRICAL WORKS | Main BOQ | 175 MVA Transformer | 2.2 | Automatic voltage regulator complete system as specified. | 42046
ELECTRICAL WORKS | Main BOQ | 175 MVA Transformer | 2.3 | Onload tap changers to regulate voltage within ±10%. | 126139
ELECTRICAL WORKS | Main BOQ | 175 MVA Transformer | 2.4 | Online early fault detection system with accessories. | 84093
MECHANICAL WORKS | Main BOQ | Fire Fighting System | 2/1.Main | Fire Fighting System
MECHANICAL WORKS | Main BOQ | Fire Fighting System | 2.5 | Firefighting system covering the existing and the future transformer. | 0 |  | 8681123
GIS - 66KV - (Annex III) | GIS - 66KV - (Annex III) |  | 3 | Lump sum price for design, fabrication, factory testing, training and site delivery of 66 kV GIS switchgear
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.Main | GIS - 66KV
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.1 | Three phase 66 kV SF6 insulated double sectionalized bus bars and connectors with all accessories. | 66300
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.2 | Local control panels associated with the 66 kV GIS switchyard bays as specified | 72377
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.3 | Three phase GIS high speed earthing switch for Bus Bar 40 kA short circuit | 26388
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.4 | Three single phase GIS inductive voltage transformer complete with its disconnector and earthing switch as specified for busbars 66 3:0.1 3:0.1 3 kV. | 31665
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.5 | Three phase GIS longitudinal bus bar disconnector with rated current 2500 A for the sectionalizer. | 42220
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.6 | Three phase GIS circuit breaker for bus coupler 2500 Amp. | 44859
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.7 | Three phase GIS busbar disconnectors for bus coupler 2500 A | 21110
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.8 | Three phase GIS maintenance earth switch for bus coupler | 26388
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.9 | Single phase current transformers for coupler bay 1250 2500 1 1 A with two protection cores. | 15833
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.01 | Single phase current transformer for coupler bay 1250 2500 1 1 A with one protection core and one measuring core. | 15833
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.11 | Three phase GIS longitudinal bus bar disconnector with rated current 2500 A complete with earth switch for future extension. | 21110
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.12 | Three phase GIS circuit breakers 1600 A for Cable feeders. | 269154
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.13 | Three phase GIS busbar disconnectors 1600 A for Cable feeders . | 126661
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.14 | Three phase GIS line disconnectors 1600 A for Cable feeders. | 63330
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.15 | Three phase GIS maintenance earthing switch for cable feeders. | 118744
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.16 | Three phase GIS high speed earthing switch for cable feeders | 39582
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.17 | Three single phase GIS inductive voltage transformer complete with its disconnector and earthing switch as specified for cable feeders 66 3:0.1 3:0.1 3 kV. | 47497
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.18 | Single phase GIS surge arresters 60 kV, 10 kA, 3.5 kJ kV along with disconnector switch. | 108000
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.19 | Single phase GIS current transformer for cable feeder bay 800 1600 1 1 1 A . | 94998
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.02 | Three phase GIS Cable End Box for cable sealing end SF6 XLPE with rated current ≥ 1600 A complete with disconnecting link with facility to install Cable Air test bushing. | 25200
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.21 | Three phase GIS circuit breakers 2000 A for 175MVA incoming transformer feeders. | 89718
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.22 | Three phase GIS busbar disconnectors 2000 A for 175MVA incoming transformer feeders . | 42220
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.23 | Three phase GIS maintenance earthing switch for 175MVA incoming transformer feeders. | 39581
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.24 | Single phase GIS inductive voltage transformer complete with its disconnector and earthing switch as specified for incoming transformer feeders 66 3:0.1 3:0.1 3 kV. | 47497
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.25 | Single phase GIS current transformer for 175MVA incoming transformer feeder 1000 2000 1 1 1 1 1 A . | 31666
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.26 | Three Single phase GIS Cable End Box for cable sealing end SF6 XLPE adequate for 2x1Cx1200mm², complete with disconnecting link with facility to install Cable Air test bushing. | 47499
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.27 | Three phase GIS circuit breakers 1600 A for 40MVA transformer feeders. | 134577
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.28 | Three phase GIS busbar disconnectors 1600 A for 40MVA transformer feeders . | 63330
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.29 | Three phase GIS maintenance earthing switch for 40MVA transformer feeders. | 59372
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.03 | Single phase GIS current transformer for 40MVA incoming transformer feeder 400 800 1 1 1 1 A . | 47499
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.31 | Three phase 66 kV SF6 insulated GIB up to the SF6 Air bushing for transformer feeders. | 65300
ELECTRICAL WORKS | Main BOQ | GIS - 66KV | 3.32 | 66 kV single phase SF6 Air bushings for transformer feeders | 11874
40 MVA Transformer - (Annex IV) | 40 MVA Transformer - (Annex IV) |  | 4 | Lump sum price for design, fabrication, factory testing, training and site delivery of two 2 three phase 66 11 kV Power Transformers each of 40 MVA
ELECTRICAL WORKS | Main BOQ | 40 MVA Transformer | 4.Main | 40 MVA Transformer
ELECTRICAL WORKS | Main BOQ | 40 MVA Transformer | 4.1 | Three-phase oil- immersed outdoor power transformers 40 MVA, 66/11 kV complete with its all accessories as specified. | 0 |  | 87588242
ELECTRICAL WORKS | Main BOQ | 40 MVA Transformer | 4.2 | Automatic voltage regulator (complete system) as specified. | 0 |  | 882818
ELECTRICAL WORKS | Main BOQ | 40 MVA Transformer | 4.3 | On-load tap changers (OLTC) for the above transformers | 0 |  | 2648454
ELECTRICAL WORKS | Main BOQ | 40 MVA Transformer | 4.4 | On-line early fault detection with its all accessories as specified. | 0 |  | 1765636
ELECTRICAL WORKS | Main BOQ | Fire Fighting System | 4.5 | Firefighting system covering the existing and the future one transformer as specified. | 0 |  | 4300000
Outdoor Equipment - (Annex V) | Outdoor Equipment - (Annex V) |  | 5 | Lump sum price for design, fabrication, factory testing, training and site delivery of 220 kV, 66 kV and 11 kV outdoor equipment
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.1 | Single phase AIS 220 kV CCVT (220/√3:0.1/√3:0.1/√3/0.1/√3kV) for outgoing OHTLs as specified. | 118164 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.2 | Single phase AIS 214 kV, 10kJ/kV, 20kA surge arresters for 220 kV outgoing OHTLs & 220 kV side of 175 MVA Power Transformers as specified. | 0 | 66658 | 0
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.3 | Single phase 220 kV wave trap for outgoing OHTLs as specified. | 72494 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.4 | Single phase AIS disconnector switch 1600 A for the neutral point of 220 kV side of 175 MVA power transformers as specified. | 20056 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.5 | Single phase AIS 108kV, 10kJ/kV, 20kA surge arresters for the 220 kV neutral point of 175 MVA Power Transformers as specified. | 0 | 6014 | 0
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.6 | Single phase current transformer (400-800 /1/1 A) for the 220 kV neutral point of 175 MVA Power Transformers as specified. | 15465 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.7 | Single phase AIS 60 kV, 4.5kJ/kV, 10kA surge arresters for 66 kV side of 175 MVA & 40 MVA Power Transformers as specified. | 0 | 19240 | 0
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.8 | Single phase AIS disconnector switch 2000 A for the neutral point of 66 kV side of 175 MVA power transformers as specified. | 9183 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.9 | Single phase AIS 30kV, 4.5kJ/kV, 10kA surge arresters for the 66 kV side neutral point of 175 MVA Power Transformers as specified. | 0 | 2750 | 0
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.01 | Single phase current transformer (1000-2000 /1/1 A) for the 66 kV neutral point of 175 MVA Power Transformers as specified. | 9183 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.11 | Single phase AIS 12kV, 2.5kJ/kV, 10kA surge arresters for the 11 kVwindings of 175 MVA & 40 MVA Power Transformers as specified. | 0 | 10961 | 0
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.12 | Single phase current transformer (1500-3000/1/1A) for the neutral point at 11 kV side of 40 MVA Power Transformers as specified. | 0 | 0 | 208370
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.13 | Single phase disconnector switch (2500A) at 11 kV neutral points as specified. | 0 | 0 | 125408
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.14 | Neutral Earthing Resistor (10 Ω, 650A, 30sec) as specified. | 0 | 0 | 963490
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.15 | Single phase AIS 9kV, 2.5kJ/kV, 10kA surge arresters at 11 kV neutral points as specified. | 0 | 0 | 10773
ELECTRICAL WORKS | Main BOQ | Outdoor Equipment | 5.16 | Copper connections (conductors), hardware fittings and accessories to connect outdoor equipment (220 kV, 66 kV, 11 kV & neutral points) to GIS bays and transformer bays with all accessories as specified. | 0 | 0 | 3800000
MV switchgear - (Annex VI) | MV switchgear - (Annex VI) |  | 6 | Lump sum price for design, fabrication, factory testing, training and site delivery of MV switchgear
ELECTRICAL WORKS | Main BOQ | MV switchgear | 6.Main | MV switchgear
ELECTRICAL WORKS | Main BOQ | MV switchgear | 6.1 | Incoming cell (3150A) including cable end boxes associated with its current & voltage transformers, protection, control, measuring and metering, including three single phase voltage transformers as specified | 0 | 0 | 1800000
ELECTRICAL WORKS | Main BOQ | MV switchgear | 6.2 | Bus riser cell 3150 A, associated with its circuit breaker, protection and metering devices (per each feeder) as specified | 0 | 0 | 1800000
ELECTRICAL WORKS | Main BOQ | MV switchgear | 6.3 | Bus coupler cell 3150 A, associated with its circuit breaker, protection and metering devices (per each feeder) as specified | 0 | 0 | 1800000
ELECTRICAL WORKS | Main BOQ | MV switchgear | 6.4 | Auxiliary transformer cells (1250A) including cable end boxes associated with its current transformers, protection, control, measuring and metering as specified | 0 | 0 | 1800000
ELECTRICAL WORKS | Main BOQ | MV switchgear | 6.5 | Outgoing cells (1250A) including cable end boxes associated with its current transformers, protection, control, measuring and metering as specified. | 0 | 0 | 25200000
ELECTRICAL WORKS | Main BOQ | MV switchgear | 6.6 | Measuring cells associated with three single phase voltage transformer provided with HRC Fuses. | 0 | 0 | 811113
ELECTRICAL WORKS | Main BOQ | MV switchgear | 6.7 | Single phase 12 kV surge arrester for bus sections as specified | 0 | 0 | 95425
ELECTRICAL WORKS | Main BOQ | MV switchgear | 6.8 | Three Single phase bus section as specified | 0 | 0 | 909828
ELECTRICAL WORKS | Main BOQ | MV switchgear | 6.9 | 11 kV capacitor bank feeder cells 1250 A, associated with its SF6/Vacuum circuit breaker, protection, control, measuring and metering (per each cell) as specified. | 0 | 0 | 1800000
ELECTRICAL WORKS | Main BOQ | MV switchgear | 6.01 | Frequency load shedding relays (one per each 11 kV bus section). | 0 | 0 | 715688
Auxiliary Power Equipment - (Annex VII) | Auxiliary Power Equipment - (Annex VII) |  | 7 | Lump sum price for design, fabrication, factory testing and site delivery of auxiliary power equipment
ELECTRICAL WORKS | Main BOQ | Auxiliary Power Equipment | 7.1 | 500 kVA auxiliary transformer 11 0.4 kV, as specified. | 0 | 0 | 1800000
ELECTRICAL WORKS | Main BOQ | Auxiliary Power Equipment | 7.2 | L.V. 0.4 kV AC main distribution board and sub distribution panels complete with switches, measuring devices as specified . | 0 | 0 | 3250000
ELECTRICAL WORKS | Main BOQ | Auxiliary Power Equipment | 7.3.1 | Accumulator battery complete | 0
ELECTRICAL WORKS | Main BOQ | Auxiliary Power Equipment | 7.3.2 | Charger rectifier set complete with it s dropper diodes, CB …etc. | 0 | 0 | 9111618
ELECTRICAL WORKS | Main BOQ | Auxiliary Power Equipment | 7.3.3 | Main distribution board complete with Bus Bar, Air Circuit Breakers for incomers and couplers , MCCBs and MCB for outgoing, cable box, etc. | 0 | 0 | 1064570
ELECTRICAL WORKS | Main BOQ | Auxiliary Power Equipment | 7.4 | 11 kV, 9 MVAr Capacitor bank units as specified.. | 205600 | 0 | 1630000
Substation Control System (SCS) - (Annex VIII) | Substation Control System (SCS) - (Annex VIII) |  | 8 | Lump sum price breakdown for contractor furnished SCS, control, metering, measuring and protection Devices
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.Main | Substation Control System (SCS)
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.1 | Substation control system SCS Servers, Operator Workstation, Engineering Workstation, Printers, Switches , gateways, Original software and Application Firmware…etc. | 285600 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.2.1 | Price for 220 kV outgoing feeders control panels as specified. | 85279 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.2.2 | Price for 220 kV side of 175 MVA, 220/66/11 kV transformer feeders control panels as specified. | 45685 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.2.3 | Price for 220 kV bus coupler and bus section feeder control panels as specified. | 5076 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.3.1 | Price for 220 kV outgoing OHTL feeders protection panels as specified. | 81218 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.3.2 | Price for 220 kV outgoing cable feeders protection panels as specified. | 40609 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.3.3 | Price for 220 kV protection panels for 175 MVA, 220/66/11 kV transformer feeders as specified (two cubicales for each). | 76142 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.3.4 | Price for 220 kV bus coupler protection panels as specified. | 15228 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.3.5 | Price for 220 kV busbar protection/Breaker Failure panels for 12 circuirt breakers as specified. | 33225 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.3.6 | Price for 220 kV metering panels as specified. | 35533 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.4.1 | Price for 66 kV side control & protection panels for 175 MVA, 220/66/11 kV transformer feeders as specified. | 68527 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.4.2 | Price for 66 kV side control & protection panels for 40 MVA, 66/11 kV transformer feeders as specified. | 68527 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.4.3 | Price for 66 kV outgoing cable feeders protection panels as specified. | 91371 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.4.4 | Price for 66 kV bus coupler control & protection panel as specified. | 15228 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.4.5 | Price for 66 kV busbar protection / Breaker failure panels for 15 circuirt breakers as specified. | 41532 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.4.6 | Price for 66 kV metering panels as specified. | 30456 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.4.7 | Price for synchronizing panel as specified. | 10152 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.4.8 | Price for general alarm panel as specified. | 5076 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.5 | 220 kV Remote end substations as specified in relevant sections. | 20305 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.6 | 66 kV Remote end substations as specified in relevant sections. | 15228 | 0 | 0
ELECTRICAL WORKS | Main BOQ | Substation Control System (SCS) | 8.7 | Any additional material and equipment required for the whole substation. | 0 | 0 | 0
Cables - (Annex IX) | Cables - (Annex IX) |  | 9 | Lump sum price for design, fabrication, factory testing and site delivery of HV, MV, LV and Control cables including CSE and necessary accessories, fittings, clamps, etc.
ELECTRICAL WORKS | Main BOQ | Cables | 9.1 | Three phase single core XLPE 38 -66 72.5 kV copper cables with cross section not less than 2×1C×1200 mm² - ph to connect the 66 kV sides of the two 175 MVA 220 -66 -11 kV transformers to 66 kV GIS switchgear | 0 |  | 5967153
ELECTRICAL WORKS | Main BOQ | Cables | 9.2 | 72.5 kV single core cable sealing end outdoor porcelain type for the above mentioned cables | 0 |  | 3117230
ELECTRICAL WORKS | Main BOQ | Cables | 9.3 | 72.5 kV single core cable sealing end XLPE -SF6 type for the above mentioned cables | 0 |  | 3692749
ELECTRICAL WORKS | Main BOQ | Cables | 9.4 | Three phase single core XLPE 12 -20 24 kV copper cables with cross section not less than 4×1C×800 mm² | 0 |  | 9577230
ELECTRICAL WORKS | Main BOQ | Cables | 9.5 | Single core cable sealing end outdoor Heat Shrinkable type for the above mentioned cables | 0 |  | 132344
ELECTRICAL WORKS | Main BOQ | Cables | 9.6 | Single core cable sealing end indoor Heat Shrinkable type for the above mentioned cables | 0 |  | 223443
ELECTRICAL WORKS | Main BOQ | Cables | 9.7 | Three phase XLPE 12 -20 24 kV copper cables with cross section not less than 3C×240 mm² - ph to connect the 11 kV sides of the two auxiliary transformers to 11 kV MV switchgear | 0 |  | 547148
ELECTRICAL WORKS | Main BOQ | Cables | 9.8 | Three phase cable sealing end indoor Heat Shrinkable type for the above mentioned cables | 0 |  | 29434
ELECTRICAL WORKS | Main BOQ | Cables | 9.9 | Three phase single core XLPE 12 -20 24 kV copper cables with cross section not less than 1x1C×630 mm² - ph to connect the 11 kV MV switchgear to the capacitor banks | 0 |  | 3014337
ELECTRICAL WORKS | Main BOQ | Cables | 9.01 | Single core cable sealing end outdoor (Heat Shrinkable) type for the above mentioned cables in item 9.9 | 0 |  | 28029
ELECTRICAL WORKS | Main BOQ | Cables | 9.11 | Single core cable sealing end indoor (Heat Shrinkable) type for the above mentioned cables in item 9.9 | 0 |  | 21922
ELECTRICAL WORKS | Main BOQ | Cables | 9.12 | Any additional equipment and materials such as L.V cables, Control cables, etc. required for the whole S -S and at remote end substations. | 0 |  | 49512600
Telecommunication System - (Annex X) | Telecommunication System - (Annex X) |  | 10 | Lump sum price for design, fabrication, factory testing, training, receiving, unloading and site delivery of telecommunication and SCADA system
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.Main | Telecommunication System
Telecommunication and SCADA system | Telecommunication and SCADA system | Telecommunication System | 10 | Lump sum price breakdown of Telecommunication for design, engineering, fabrication, FAT and site delivery Items (10) |  |  | 0
ELECTRICAL WORKS | Telecommunication and SCADA system | Telecommunication System | 10.1.1 | Line matching unit | 0 | 147905 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.1.2 | Co-axial cable complete with accessories as specified for PS3-220 kV S -S and remote sites Zahraa Al-Maadi and Korimate 220 kV | 0 | 12918 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.1.3 | DPLC equipment with Multiplexers at PS3 220 kV S -S and remote sites Zahraa Al-Maadi and Korimate 220 kV | 0 | 318368 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.1.4 | Teleprotection Tone equipment at PS3 220 kV S -S and remote sites Zahraa Al-Maadi and Korimate 220 kV | 0 | 232246 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.1.5 | Stand alone cabinets for DPLC | 0 | 234253 | 0
Main BOQ | Main BOQ | Telecommunication System | 10.2 | Price for Supply of the Fiber Optic System including standalone cabinets supports MPLS-TP/ 1 Gbps & MPLS-TP/ 10 Gbps Fiber terminal equipment For PS3-220/66/11 S/S and remote sites [Zahraa Al-Maadi & Korimat 220 kV S/Ss]& [PS2 & PS4 66 kV S/Ss] as specified: |  |  | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.2.1 | MPLS-TP 1Gbps Fiber Optic Equipment Siemens Infinera 7090-100 CEM with 4 SFP modules | 0 | 45932 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.2.2 | Digital Teleprotection equipment at PS3-220 -66 -11 kV S -S | 0 | 86123 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.2.3 | SFP modules for the existing Fiber Optic Equipment Siemens Infinera 7090-100 CEM at Zahraa Al-Maadi 220 kV S -S and Korimat 220 kV S -S | 0 | 34450 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.2.4 | MPLS-TP -10 Gbps Fiber Optic Equipment Huawei OSN 1800 platform with 4 SFP modules | 0 | 17224 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.2.5 | SFP modules for the existing Fiber Optic Equipment Huawei OSN 1800 platform at PS2 66kV S -S and PS4 66kV S -S | 0 | 34450 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.2.6 | Standalone cabinets | 0 | 48700 | 0
Main BOQ | Main BOQ | Telecommunication System | 10.3 | Supply of the Telephone System at PS3 220/66/11 kV Substation S/S, as specified: |  |  | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.3.1 | Telephone sets type Analog Desktop | 0 | 3013 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.3.2 | Telephone sets type IP phones. | 0 | 1722 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.3.3 | Media Gateways with its license for PS3 220 kV | 0 | 430 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.3.4 | Media Gateways with its license for PS3 66 kV | 0 | 861 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.3.5 | New Router Siemens Ruggedcom RX1501 | 0 | 861 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.3.6 | RS232 cards LM S01 at existing Siemens Ruggedcom RX1501 routers at remote sites Zahraa El Maadie and korimat | 0 | 1600 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.4 | Main distribution frame - Digital distribution frame MDF -DDF with wall mounted cabinet at PS3 220 -66 -11 kV Substation S -S | 0 | 24114 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.5 | Miscellaneous cables, accessories, auxiliaries..etc required to complete the job. | 0 | 32600 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10/1.Main | 48 V DC System
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.6 | Supply of 48 V DC System at PS3-220 -66 -11kV S -S |  | 0 | 0
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.6.1 | Battery bank with racks | 0 | 0 | 2300000
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.6.2 | Battery charger complete with control and protection | 0 | 0 | 355255
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.6.3 | Moulded case circuit breaker MCCB. | 0 | 0 | 19736
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.6.4 | Dropping diodes. | 0 | 0 | 7895
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.6.5 | Low voltages disconnect LVD | 0 | 0 | 11842
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.6.6 | 48 V DC main distribution board complete with switches, measuring device, etc. | 0 | 0 | 365000
ELECTRICAL WORKS | Main BOQ | Telecommunication System | 10.6.7 | AC sub-distribution panel at the telecommunication room | 0 | 0 | 165000
Civil Works (Annex XI). | Civil Works (Annex XI). |  | 11 | Lump sum price for civil works
CIVIL WORKS | Main BOQ | Civil Works | 11.Main | Civil Works Breakdown
CIVIL WORKS | Main BOQ | Civil Works | 11.1 | Site leveling and final zero level of the substation | 0 | 0 | 17884220
CIVIL WORKS | Main BOQ | Structural steel works | 11.2 | Foundations and steel structure for the outdoor equipment and receiving gantries | 0 | 0 | 12058882
CIVIL WORKS | Main BOQ | Civil Works | 11.3 | Concrete works for 220 kV GIS building | 0 | 0 | 21340023
CIVIL WORKS | Main BOQ | Civil Works | 11.4 | Architectural works for 220 kV GIS building | 0 | 0 | 11348564
MECHANICAL WORKS | Main BOQ | Overhead crane | 11.5 | Overhead crane for 220 kV GIS building | 0 | 0 | 10144495
CIVIL WORKS | Main BOQ | Civil Works | 11.6 | Concrete Works for 66 kV GIS Building | 0 | 0 | 12648048
CIVIL WORKS | Main BOQ | Civil Works | 11.7 | Architectural Works for 66 kV GIS Building | 0 | 0 | 7420147
CIVIL WORKS | Main BOQ | Overhead crane | 11.8 | Overhead crane for 66 kV GIS building | 0 | 0 | 3933993
CIVIL WORKS | Main BOQ | Civil Works | 11.9 | Transformer's Foundations For Two Nos of 220-66-11 kV Transformers and Three Nos of 66-11 kV transformers with fire protective walls considering spaces for the future 220-66 kV one | 0 | 0 | 37732513
CIVIL WORKS | Main BOQ | Civil Works | 11.01 | OIL PITS- one for 220-66-11 kV Power Tr.s and other one for 66-11 kV Power Trs. | 0 | 0 | 6576736
CIVIL WORKS | Main BOQ | Civil Works | 11.11 | Concrete Works for Control Building including M.V room with basement | 0 | 0 | 38580059
CIVIL WORKS | Main BOQ | Civil Works | 11.12 | Architectural Works for Control Building | 0 | 0 | 40167912
CIVIL WORKS | Main BOQ | Civil Works | 11.13 | Firefighting Building and foundation for the pressurized Steel Water Tanks for 220-66-11 kV Tr.s and other fire fighting room and foundation for the pressurized steel tank for 66-11 kV Tr.s | 0 | 0 | 3993018
CIVIL WORKS | Main BOQ | Cable Trenches and Ducts | 11.14 | External Cable Trenches and Ducts for the power and control cables including cable trenches and ducts for M.V cables up to the boundary wall including the required extension-s for the cable trenches | 0 | 0 | 20268710
CIVIL WORKS | Main BOQ | Civil Works | 11.15 | Galvanized Steel Fence Wire Mesh around the transformers, Capacitor banks and outdoor equipment | 0 | 0 | 1905166
CIVIL WORKS | Main BOQ | Civil Works | 11.16 | Roads main, secondary and access for the substation | 0 | 0 | 17353987
CIVIL WORKS | Main BOQ | Civil Works | 11.17 | Two new sides of boundary wall and rehabilitation works for the other two existing sides | 0 | 0 | 10439263
CIVIL WORKS | Main BOQ | Civil Works | 11.18 | Guard Room | 0 | 0 | 2609816
CIVIL WORKS | Main BOQ | Civil Works | 11.19 | Guard Towers | 0 | 0 | 3914724
CIVIL WORKS | Main BOQ | Civil Works | 11.02 | Shed Roof for Vehicles and capacitor banks | 0 | 0 | 7829447
CIVIL WORKS | Main BOQ | Civil Works | 11.21 | Foundations and wire mesh fence for the Capacitor Banks | 0 | 0 | 469767
CIVIL WORKS | Main BOQ | Civil Works | 11.22 | Water Supply System including the underground water tank | 0 | 0 | 2609816
MECHANICAL WORKS | Main BOQ | Fire Hydrant System | 11.23 | Firefighting Line System Fire Hydrant System including pumps room | 0 | 0 | 12044952
MECHANICAL WORKS | Main BOQ | Sewage System | 11.24 | Sewage System | 0 | 0 | 4352882
CIVIL WORKS | Main BOQ | Civil Works | 11.25 | Sanitary Installations | 0 | 0 | 2609816
ELECTRICAL WORKS | Main BOQ | Earthing and Lightning System | 11.26 | Earthing and Lightning System for the substation | 0 | 0 | 37272019
MECHANICAL WORKS | Main BOQ | Fire Alarm and Fire Detection System | 11.27 | Fire Alarm and Fire Detection System | 0 | 0 | 1454255
MECHANICAL WORKS | Main BOQ | HVAC | 11.28 | Ventilation and Air-Conditioning System | 0 | 0 | 11904248
ELECTRICAL WORKS | Main BOQ | Security System | 11.29 | Substation Security System | 0 | 0 | 1650000
ELECTRICAL WORKS | Main BOQ | Lighting | 11.03 | Indoor and Outdoor Lighting | 0 | 0 | 6524539
CIVIL WORKS | Main BOQ | Civil Works | 11.31 | Mobilization and De-mobilization | 0 | 0 | 2609816
Installing, start up testing and commissioning (Annex XII). | Installing, start up testing and commissioning (Annex XII). |  | 13 | Lump sum price for installing, start up testing and commissioning of the substation 220-66-11 kV
ELECTRICAL WORKS | Main BOQ | Installing, start up testing and commissioning | 13.Main | Installing, start up testing and commissioning
ELECTRICAL WORKS | Main BOQ | Installing, start up testing and commissioning | 13.1 | Installing, start up testing and commissioning of 220 kV GIS switchgear | 0 | 0 | 6838004
ELECTRICAL WORKS | Main BOQ | Installing, start up testing and commissioning | 13.2 | Installing, startup testing and commissioning of 220-66-11 kV main transformers with its firefighting and neutral point equipment | 0 | 0 | 5644067
ELECTRICAL WORKS | Main BOQ | Installing, start up testing and commissioning | 13.3 | Installing, start up testing and commissioning of 66 kV GIS switchgear | 0 | 0 | 6450361
ELECTRICAL WORKS | Main BOQ | Installing, start up testing and commissioning | 13.4 | Installing, startup testing and commissioning of 66-11 kV main transformers with its firefighting and neutral point equipment | 0 | 0 | 2650000
ELECTRICAL WORKS | Main BOQ | Installing, start up testing and commissioning | 13.5 | Installing, startup, testing and commissioning of 11 kV MV switchgear | 0 | 0 | 881885
ELECTRICAL WORKS | Main BOQ | Installing, start up testing and commissioning | 13.6 | Installing, startup testing and commissioning of the auxiliary power equipment | 0 | 0 | 2633897
ELECTRICAL WORKS | Main BOQ | Installing, start up testing and commissioning | 13.7 | Installing, start up testing and commissioning of control, metering, measuring, protection and SCS systems | 0 | 0 | 4891524
ELECTRICAL WORKS | Main BOQ | Installing, start up testing and commissioning | 13.8 | Installing, startup, testing and commissioning of cables of the Substation | 0 | 0 | 1881355
ELECTRICAL WORKS | Main BOQ | Installing, start up testing and commissioning | 13.9 | Installing, startup, testing and commissioning of Telecommunication System | 0 | 0 | 3010168
ELECTRICAL WORKS | Main BOQ | Installing, start up testing and commissioning | 13.01 | Installing, startup, testing and commissioning of Miscellaneous Systems | 0 | 0 | 3386440
Spare Parts | Spare Parts |  | 14 | Spare Parts
14.1 Spare Parts For GIS - 220KV | 14.1 Spare Parts For GIS - 220KV |  | 14.1 | 220 kV Switchgear GIS
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.1.1 | Three single phase circuit breaker complete with mechanism in enclosure from each type. | 87903 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.1.2 | Set of gaskets for three pole CB mechanism | 7249 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.1.3 | Set of tripping and closing coils per mechanism. | 5998 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.1.4 | Sets of Aux. Switches for CB | 6814 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.1.5 | Motor with oil pump for operation mechanism for hydraulic mechanism CB.
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.1.6 | Complete three phase motor spring mechanism for motor spring operating mechanism C.B | 6814 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.2 | Disconnectors and Earthing switches | 33403 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.2.1 | Three single pole disconnector switch complete with mechanism in enclosure from each type. | 11720 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.2.2 | Three pole maintenance earthing switch complete with mechanism in enclosure from each type. | 13628 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.2.3 | Set of Aux. Switches for disconnector and earthing switches. | 10904 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.2.4 | Motor for operating mechanism for disconnector and earthing switch. | 4798 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.2.5 | Set of opening and closing relays for disconnector and earthing switch. | 8790 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.2.6 | Three single phase high speed earthing switch complete with mechanism in enclosure. | 43952 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.4 | Single pole SF6 inductive VT with enclosure. | 21975 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.5 | Set of oil monitoring devices per mechanism.
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.6.1 | Per line bay | 2029 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.6.2 | Per coupler. | 2029 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.6.3 | Per transformer bay | 2029 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.6.4 | Per bus bar section | 2029 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.6.5 | Per connecting bus bar | 2029 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.7 | Set gas barriers complete with connections. | 3625 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.8 | Set of enclosure gaskets | 7249 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.9 | Single phase SF6 air bushing complete with enclosure. | 7325 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.01 | Single phase cable box for SF6 XLPE cable sealing end. | 30000 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.11 | Single phase GIS surge Arresters | 8000 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.12 | Set of temperature compensating bellows. | 2416 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.2.13 | Set of gas filler for one bay | 1208 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.14 | Set of pressure relief devices. | 725 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.15 | Set of SF6 pipes per bay. | 6041 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.16 | SF6 gas bottles of 40 kg. size. | 12082 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 220KV | 14.1.17 | Single phase SF6 surge arresters complete (as applicable). | 8000 | 0 | 0
14.2 Spare Parts For GIS - 66KV | 14.2 Spare Parts For GIS - 66KV |  | 14.2 | 66 kV Switchgear GIS
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.1.1 | Three phase circuit breaker complete with mechanism in enclosure of each rating. | 44859 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.1.2 | Set of gaskets for three pole CB mechanism | 4350 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.1.3 | Set of tripping and closing coils per mechanism. | 4798 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.1.4 | Sets of Aux. Switches for CB | 5452 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.1.5 | Motor with oil pump for operation mechanism for hydraulic mechanism CB.
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.1.6 | Complete three phase motor spring mechanism for motor spring operating mechanism C.B | 5452 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.2.1 | Three single pole disconnector switch complete with mechanism in enclosure from each type. | 10555 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.2.2 | Three pole maintenance earthing switch complete with mechanism in enclosure from each type. | 6597 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.2.3 | Set of Aux. Switches for disconnector and earthing switches. | 10904 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.2.4 | Motor for operating mechanism for disconnector and earthing switch. | 8722 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.2.5 | Set of opening and closing relays for disconnector and earthing switch. | 3838 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.2.6 | Three single phase high speed earthing switch complete with mechanism in enclosure. | 6597 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.3 | Single phase current transformer (one of each ratio) with enclosure. | 10555 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.4 | Single pole SF6 inductive VT with enclosure. | 7917 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.5 | Set of oil monitoring devices per mechanism.
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.6.1 | Per line bay
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.6.2 | Per coupler.
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.6.3 | Per transformer bay
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.6.4 | Per bus bar section
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.6.5 | Per connecting bus bar
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.7 | Set gas barriers complete with connections. | 2900 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.8 | Set of enclosure gaskets | 4350 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.9 | Single phase SF6/air bushing complete with enclosure (from each type). | 1319 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.01 | Single phase cable box for SF6/XLPE cable sealing end. | 5278 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.11 | Single phase GIS surge Arresters | 6000 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.12 | Set of temperature compensating bellows. | 1933 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.13 | Set of gas filler for one bay | 967 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.2.14 | Set of pressure relief device (of each type). | 580 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.15 | Set of SF6 pipes per bay. | 4833 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.16 | SF6 gas bottles of 40 kg. size. | 12082 | 0 | 0
ELECTRICAL WORKS | Spare Parts | GIS - 66KV | 14.1.17 | Single phase SF6 surge arresters complete (as applicable). | 12000 | 0 | 0
14.3 Spare Parts For 175 MVA Transformer | 14.3 Spare Parts For 175 MVA Transformer |  | 14.3 | 175 MVA Transformer
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.2 | a) 220 kV Line terminal | 28998 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.3 | b) 66 kV Line terminal | 13290 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.4 | c) 11 kV Tertiary terminal | 3600 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.5 | d) 220 kV Neutral point | 10874 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.6 | e) 66 kV Neutral point
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.7 | Cooling fan complete with motor | 2416 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.8 | Set of one of each type of relays and measuring instruments | 6645 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.9 | Set of relief vent diaphragms of each type | 9666 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.01 | Complete set of on-load tap changer contacts complete with spring
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.11 | Complete set of gaskets together with gaskets cement for one transformer | 7249 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.12 | Complete breath set | 8458 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.13 | Complete mechanism with motor for O.L.T.C | 2416 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.14 | Motor drive for cooling fans
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.15 | Set of Buchholz relay | 5135 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.16 | Set of temp. indicator for oil & winding | 7249 | 0 | 0
ELECTRICAL WORKS | Spare Parts | 175 MVA Transformer | 14.3.17 | oil equivalent to 25 % of the first filling for one transformer | 45000 | 0 | 0
14.4 Spare Parts For 40 MVA Transformer | 14.4 Spare Parts For 40 MVA Transformer |  | 14.4 | 40 MVA Transformer
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.2 | a) 66 kV Line terminal | 0 | 0 | 280000
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.3 | b) 11 kV Line terminal | 0 | 0 | 210000
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.4 | c) 11 kV Neutral point | 0 | 0 | 140000
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.5 | Cooling fan complete with motor | 0 | 0 | 110000
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.6 | Set of one of each type of relays and measuring instruments | 0 | 0 | 290000
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.7 | Set of relief vent diaphragms of each type | 0 | 0 | 380000
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.8 | Complete set of on-load tap changer contacts complete with spring | 0 | 0
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.9 | Complete set of gaskets together with gaskets cement for one transformer | 0 | 0 | 179000
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.01 | Complete breath set | 0 | 0 | 280000
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.11 | Complete mechanism with motor for O.L.T.C | 0 | 0 | 95000
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.12 | Motor drive for cooling fans | 0 | 0
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.13 | Set of Buchholz relay | 0 | 0 | 175000
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.14 | Set of temp. indicator for oil & winding | 0 | 0 | 240000
ELECTRICAL WORKS | Spare Parts | 40 MVA Transformer | 14.4.15 | oil equivalent to 25 % of the first filling for one transformer | 0 | 0 | 850000
14.5 Spare Parts For MV Switchgear | 14.5 Spare Parts For MV Switchgear |  | 14.5 | 11 kV MV Switchgear
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.1 | Transformer incoming circuit breaker rated 3150 A complete with its truck. | 0 | 0 | 375000
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.2 | Outgoing feeder circuit breaker rated 1250A complete with its truck. | 0 | 0 | 375000
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.3 | Bus section circuit breaker rated 3150 A complete with its truck. | 0 | 0 | 375000
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.4 | Sets of each of fixed and moving contacts for3150 A circuit breaker of the bus section feeder. | 0 | 0 | 8216
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.5 | Sets of each of fixed and moving contacts for 3150 A circuit breaker of the transformer incoming feeder. | 0 | 0 | 8216
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.6 | Sets of each of fixed and moving contacts for 1250 A circuit breaker of the outgoing feeder. | 0 | 0 | 8216
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.7 | Portable detector for SF6 leakage. | 0 | 0 | 18123
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.8 | Complete circuit breaker mechanisms (assembled), including anti-pumping relays. | 0 | 0 | 149700
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.9 | Closing coils. | 0 | 0 | 5437
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.01 | Tripping coils. | 0 | 0 | 5437
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.11 | Three phase Potential transformers with ratio 11/√3/0.1/√3/0.1/√3 kV | 0 | 0 | 162000
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.12 | Three phase current transformers of each rating supplied according to S.L.D. | 0 | 0 | 187000
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.13 | Complete earthing switch. | 0 | 0 | 140400
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.14 | Different type of 11 kV insulators used for switchgear. | 0 | 0 | 25600
ELECTRICAL WORKS | Spare Parts | MV Switchgear | 14.5.15 | Complete set of indicating lamps (lamp included). | 0 | 0 | 4833
14.6 Spare Parts For Outdoor Equipment | 14.6 Spare Parts For Outdoor Equipment |  | 14.6 | Outdoor Equipment
ELECTRICAL WORKS | Spare Parts | Outdoor Equipment | 14.6.1 | One single phase 220 kV surge arrester | 0 | 3703 | 0
ELECTRICAL WORKS | Spare Parts | Outdoor Equipment | 14.6.2 | One single phase 220 kV neutral point surge arrester | 0 | 3007 | 0
ELECTRICAL WORKS | Spare Parts | Outdoor Equipment | 14.6.3 | One single phase 220 kV CCVT with ratio 220/√3/0.1/√3/0.1/√3/0.1/√3 kV. | 9847 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Outdoor Equipment | 14.6.4 | One single phase 220 kV neutral point Current Transformer | 7733 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Outdoor Equipment | 14.6.5 | One single phase 66 kV surge arrester | 0 | 1603 | 0
ELECTRICAL WORKS | Spare Parts | Outdoor Equipment | 14.6.6 | One single phase 66 kV neutral point surge arrester | 0 | 1375 | 0
ELECTRICAL WORKS | Spare Parts | Outdoor Equipment | 14.6.7 | One single phase 66 kV neutral point Current Transformer | 4591 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Outdoor Equipment | 14.6.8 | One single phase 11 kV surge arrester | 0 | 950 | 0
ELECTRICAL WORKS | Spare Parts | Outdoor Equipment | 14.6.9 | One single phase 11 kV neutral point surge arrester | 0 | 0 | 5200
ELECTRICAL WORKS | Spare Parts | Outdoor Equipment | 14.6.01 | One single phase 11 kV neutral point Current Transformer | 0 | 0 | 110500
14.7 Spare Parts For Substation Control System (SCS) | 14.7 Spare Parts For Substation Control System (SCS) |  | 14.7 | Control, Metering and Protection
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.7.1 | One type of each relay & BCU/FM offered type for each 66, 220 and 22(11) kV level. | 5288 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.7.2 | One type of each test block/switch. | 423 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.7.3 | 10% of spare-terminal used in the offered panels. | 423 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.7.4 | One of each type of metering instrument. | 3596 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.7.5 | One of each type of measuring instruments | 2750 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.7.6 | 10% of signal lamps. | 1058 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.7.7 | 10% of each type of auxiliary (trip relay, lockout relay T.C.S, DC supervision, bi stable, contactor etc.). | 2115 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.7.8 | One bus bar/BF bay unit | 4230 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.7.9 | One set of auxiliary switches from each supplied type | 1269 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.7.01 | One portable laptop | 1200 | 0 | 0
14.8 Spare Parts For Substation Control System (SCS) | 14.8 Spare Parts For Substation Control System (SCS) |  | 14.8 | Substation Control System SCS
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.8.1 | Monitor from the supplied offered types. | 635 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.8.2 | BCU having maximum number of digital and analogue I/Ps & O/Ps cards from the supplied offered types for each voltage level. | 7403 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.8.3 | (FM) from the supplied offered types for medium voltage. | 3807 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.8.4 | Workstation | 423 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.8.5 | Solid State Drives (SSD 1 TB) | 634 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.8.6 | Power Supply for Server and one for Workstation | 1269 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.8.7 | Gateway | 1692 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.8.8 | Ethernet Switch | 1058 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.8.9 | Server | 1481 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.8.01 | GPS system with antenna | 2115 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Substation Control System (SCS) | 14.8.11 | The Contractor shall submit at least 10% spare parts from interfacing cables (optical & electrical), etc. | 635 | 0 | 0
14.9 Spare Parts For Auxiliary Power Equipment | 14.9 Spare Parts For Auxiliary Power Equipment |  | 14.9 | Auxiliary Equipment
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.9.1 | Complete air circuit breaker of each size supplied. | 0 | 0 | 107532
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.9.2 | Complete miniature C.B and molded case C.B of each size | 0 | 0 | 6041
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.9.3 | Sets of contacts for the air circuit breaker supplied. | 0 | 0 | 2416
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.9.4 | Instrument of each type of the 380- volt switchboard. | 0 | 0 | 1208
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.9.5 | Set of 30% Signal lamp. | 0 | 0 | 3625
14.01 Spare Parts For Auxiliary Power Equipment | 14.01 Spare Parts For Auxiliary Power Equipment |  | 14.01 | 220 V DC System
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.01.1 | One of each type of cards / modules of each system. | 0 | 0 | 4839
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.01.2 | Battery cells. | 2590 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.01.3 | LVD relays. | 0 | 0 | 1075
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.01.4 | One of each relay type used in each system. | 0 | 0 | 2688
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.01.5 | Special Cables, sockets, adapter, cell connectors, etc. | 457 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.01.6 | 10% of Consumable lamps, fuses, special cable | 0 | 0 | 21500
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.11.1 | Control box | 12300 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.11.2 | Capacitor unit | 31414 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.11.3 | CB and accessories | 19544 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Auxiliary Power Equipment | 14.11.4 | Spare for control and protection relays | 7853 | 0 | 0
14.12 Spare Parts For Telecommunication system | 14.12 Spare Parts For Telecommunication system |  | 14.12 | Telecommunication Equipment
ELECTRICAL WORKS | Spare Parts | Telecommunication system | 14.12.1 | A set of 10 Percent of each supplied module | 0 | 4350 | 0
ELECTRICAL WORKS | Spare Parts | Telecommunication system | 14.12.2 | One set of all special cables and sockets connectors, adapters, etc should be included in the spare parts list. | 0 | 2610 | 0
ELECTRICAL WORKS | Spare Parts | Telecommunication system | 14.12.3 | Consumable spares, i.e. lamps, fuses, …etc., should be supplied by the contractor. It should cover 30 Percent of all types mentioned. | 0 | 1740 | 0
ELECTRICAL WORKS | Spare Parts | Telecommunication system | 14.12.4 | For chargers and Battery 48 V DC System :
ELECTRICAL WORKS | Spare Parts | Telecommunication system | 14.01.1 | One of each type of cards modules of each system. | 0 | 0 | 1794
ELECTRICAL WORKS | Spare Parts | Telecommunication system | 14.01.2 | Battery cells. | 171 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Telecommunication system | 14.01.3 | LVD relays. | 0 | 0 | 399
ELECTRICAL WORKS | Spare Parts | Telecommunication system | 14.01.4 | One of each relay type used in each system. | 0 | 0 | 997
ELECTRICAL WORKS | Spare Parts | Telecommunication system | 14.12.6 | Four Battery cell, | 30 | 0 | 0
ELECTRICAL WORKS | Spare Parts | Telecommunication system | 14.12.01 | One set of Consumable lamps, fuses, special cables. | 0 | 0 | 797
14.13 Spare Parts For Water Firefighting | 14.13 Spare Parts For Water Firefighting |  | 14.13 | Water Firefighting
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.1.1 | Pressure gauge | 0 | 0 | 60411
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.1.2 | Safety valve | 0 | 0 | 181234
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.1.3 | Water level indicator | 0 | 0 | 181234
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.1.4 | Set of gaskets, valves | 0 | 0 | 15103
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.2.1 | Complete Compressor with motor | 0 | 0 | 302057
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.2.2 | Complete Pump station with motor | 0 | 0 | 3014149
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.2.3 | Deluge valve | 0 | 0 | 120823
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.2.4 | Set of valves (one of each type & size) | 0 | 0 | 60411
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.2.5 | Pressure switches (one of each type & size) | 0 | 0 | 90617
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.2.6 | Set of gaskets (one of each type & size) | 0 | 0 | 15103
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.3.1 | Detectors (melting nozzle) | 0 | 0 | 28998
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.3.2 | Detectors (electric) | 0 | 0 | 21747
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.13.3.3 | Nozzles of each type | 0 | 0 | 21748
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.1.1 | Pressure gauge | 0 | 0 | 60411
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.1.2 | Safety valve | 0 | 0 | 181234
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.1.3 | Water level indicator | 0 | 0 | 181234
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.1.4 | Set of gaskets, valves | 0 | 0 | 15103
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.2.1 | Complete Compressor with motor | 0 | 0 | 302057
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.2.2 | Complete Pump station with motor | 0 | 0 | 3014149
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.2.3 | Deluge valve | 0 | 0 | 120823
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.2.4 | Set of valves (one of each type & size) | 0 | 0 | 60411
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.2.5 | Pressure switches (one of each type & size) | 0 | 0 | 90617
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.2.6 | Set of gaskets (one of each type & size) | 0 | 0 | 15103
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.3.1 | Detectors (melting nozzle) | 0 | 0 | 28998
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.3.2 | Detectors (electric) | 0 | 0 | 21747
ELECTRICAL WORKS | Spare Parts | Fire Fighting System | 14.14.3.3 | Nozzles of each type | 0 | 0 | 21748
15. Owner Recommended Special Tools | 15. Owner Recommended Special Tools |  | 15 | Special Tools
ELECTRICAL WORKS | Special Tools | GIS - 220KV | 15.1 | SF6 gas handling trolley suitable for the compartments and CBs of the supplied 220 kV & 66 kV GIS, complete with all accessories such as hoses, valves manometers, storage tank (capacity of not less than 100 kg and 0.5 m bar vacuum), etc., for filling, evacuation, discharge, storing, regeneration, etc. | 27600 | 0 | 0
ELECTRICAL WORKS | Special Tools | GIS - 220KV | 15.2 | Complete set of tools necessary for maintenance and adjustment of 220 kV GIS equipment. | 4832 | 0 | 0
ELECTRICAL WORKS | Special Tools | GIS - 66KV | 15.3 | Complete set of tools necessary for maintenance and adjustment of 66 kV GIS equipment. | 4832 | 0 | 0
ELECTRICAL WORKS | Special Tools | Special Tools | 15.4 | Complete set of special tools for transformer maintenance, disassemble/assemble and overhauling of OLTC | 0 | 0 | 287739
ELECTRICAL WORKS | Special Tools | Special Tools | 15.5.1 | Vacuum pump: | 39000 | 0 | 0
ELECTRICAL WORKS | Special Tools | Special Tools | 15.5.2 | Flow in (m³/h)≥300
ELECTRICAL WORKS | Special Tools | Special Tools | 15.5.3 | Vacuum during treatment (in mill-bars)≥5
ELECTRICAL WORKS | Special Tools | Special Tools | 15.5.4 | Ultimate vacuum against closed section (in mill-bars)≥0.08
ELECTRICAL WORKS | Special Tools | Special Tools | 15.5.4 | The gauge is TORR
ELECTRICAL WORKS | Special Tools | Special Tools | 15.6 | Winding and oil indication calibration device | 12082 | 0 | 0
ELECTRICAL WORKS | Special Tools | Special Tools | 15.7 | 12000 L/Hour oil purification plant, complete with hoses, filters, receivers, paper, vacuum system, etc. | 0 | 22000 | 0
ELECTRICAL WORKS | Special Tools | Special Tools | 15.8 | Complete set of battery maintenance and tests. | 5195 | 0 | 0
ELECTRICAL WORKS | Special Tools | Special Tools | 15.9 | Temporary grounding equipment set shall be comprised of: | 0 | 0 | 287740
ELECTRICAL WORKS | Special Tools | Special Tools | 15.9.1 | Grounding jumpers (clamps, ferrules, chain, etc.).
ELECTRICAL WORKS | Special Tools | Special Tools | 15.9.2 | Grounding rod, electrodes
ELECTRICAL WORKS | Special Tools | Special Tools | 15.9.3 | Grounding cluster bars.
ELECTRICAL WORKS | Special Tools | Special Tools | 15.9.4 | Rubber gloves, blankets.
16. Owner Recommended Testing Equipment | 16. Owner Recommended Testing Equipment |  | 16 | Testing Equipment
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.1 | Portable set complete with all accessories sensors and adaptors for detection, measuring recording and analysis the partial discharges in GIS equipment using the built in partial discharge sensors and the external sensors. | 28816 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.2 | Portable set complete with all accessories of ultrasonic equipment for detecting, measuring and locating of partial discharges at high voltage switchgear and equipment as specified. | 0 | 10476 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.3 | Complete set of circuit breaker analyzer with motion analyzer and all accessories as specified in Annex (2) | 19275 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.4 | SF6 decomposition product measuring device | 11236 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.5 | Dew point measuring device. | 6773 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.6 | Megger (5000 V) with battery for insulation testing complete with all accessories. | 5195 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.7 | Complete set of circuit breaker analyzer with motion analyzer and all accessories as specified. | 19275 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.8 | SF6 decomposition product measuring device | 11236 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.9 | Dew point measuring device. | 6773 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.01 | Insulation tester (motorized megger with battery) (250-600-1000-2000-2500 and 5000 V by selector) | 5195 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.11 | Phase rotation checker | 422 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.12 | D.C earth testers. | 12082 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.13 | One computer aided test set. | 62828 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.14 | Clip PF meter | 725 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.15 | Micro-ohm meter. | 10874 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.16 | Earth leakage indicator clip-on type. | 804 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.17 | Primary current injection test sets (0-3000A) with its accessories (cables, clamps and meters) | 16300 | 0 | 0
ELECTRICAL WORKS | Testing Equipment | Testing Equipment | 16.18 | Transformer oil analysis tester | 21550 | 0 | 0
17. Lump Sum Price for On-Shore training of Owner`s personnel in accordance with Tender Document. | 17. Lump Sum Price for On-Shore training of Owner`s personnel in accordance with Tender Document.
ELECTRICAL WORKS | Main BOQ | Off-Shore training | 17 | Lump Sum Price for On-Shore training of Owner`s personnel in accordance with Tender Document.
18. Lump Sum Price for Off-Shore training of Owner`s personnel in accordance with Tender Document. | 18. Lump Sum Price for Off-Shore training of Owner`s personnel in accordance with Tender Document.
ELECTRICAL WORKS | Main BOQ | Off-Shore training | 18 | Lump Sum Price for Off-Shore training of Owner`s personnel in accordance with Tender Document. | 178421 | 0 | 2452543
19. Services | 19. Services |  | SER | Services
ELECTRICAL WORKS | Main BOQ | Engineering | SER.1 | Engineering
ELECTRICAL WORKS | Main BOQ | Equipment FAT | SER.2 | Equipment FAT
20. Direct Equipment | 20. Direct Equipment
ELECTRICAL WORKS | Main BOQ | Direct Equipment | EQU | Direct Equipment